系統資料流說明書

system DataFlow Diagram

R1-SSA-PLN-001 Security Planning

2025年4月1日

ICP Taiwan

Copyright © 2025 ICP Corp. All Rights Reserved.

Content

1.	Introduction	4

1.1.	Purpose and Objectives	4

1.2.	Scope of application	4

1.3.	Glossary of Term and Definitions	5

1.4.	Abbreviations	6

1.5.	Applicable Documents	8

1.5.1.	Related Documents	8

2.	Project Asset and SuC Description	8

2.1.	System Under Consideration	8

2.2.	The Assets of SuC	11

2.2.1.	SCADA System	11

2.2.2.	Safety Control System	11

2.2.3.	Configuration & Auxiliary Management System	12

2.3.	HLRA updated Network Diagram	12

2.4.	SuC dataflow diagram	13

3.	Defense-in-Depth Architecture of the SuC	20

3.1.	From Outside Zone to Purdue Level 3	20

3.2.	From Purdue Level 3 to Purdue Level 2	21

3.3.	From Purdue Level 2 to Purdue Level 1	21

Release and Revision History

| Version | Release Date | Effective Date | Description |
| --- | --- | --- | --- |
| 1.0 | April 1, 2025 |  | Initial release of the document. |

Introduction

Purpose and Objectives

The purpose of this document is to provide a detailed description of the System Data Flow Diagram for the ICP 2L Laboratory project. It outlines the structure and flow of data within the system, offering a clear understanding of the project's data handling processes. Additionally, this document includes an updated network diagram, reflecting the results of the initial level risk assessment (ILRA), also known as the Threat and Preliminary Risk Assessment, conducted for the ICP 2L Laboratory project.

Scope of application

The System under Consideration (SuC) encompasses the power switch control system and the associated networks of the substation. The scope of systems covered by this management plan includes the following:

- Power SCADA system

- Safety Control system

- Configuration & Auxiliary Management system

Glossary of Term and Definitions

| Term | Description |
| --- | --- |
| Asset Owner | An individual or organization responsible for managing one or more Industrial Automation and Control Systems (IACS). |
| Automation Solution | A control system along with any complementary hardware and software components, all installed and configured to operate within an IACS. |
| Component | A part or element that contributes to the overall structure of a product or system. |
| Dependent Component | An external component that a product or system relies on for its operation. |
| Integration Service Provider | A service provider responsible for integration activities related to an Automation Solution, including design, installation, configuration, testing, commissioning, and handover. |
| Maintenance Service Provider | A service provider that offers ongoing support and maintenance for an Automation Solution following handover. |
| Product Supplier | A manufacturer of hardware and/or software products. |
| Recovery Point Objective (RPO) | The maximum allowable period of data loss in the event of a disaster (e.g., data corruption). |
| Recovery Time Objective (RTO) | The maximum length of time that system components or operational functions can be in a recovery phase without adversely affecting the organization’s mission or business operations. |
| Service Provider | An individual or organization (either internal or external, including manufacturers) that offers specific support services and associated supplies under an agreement with the asset owner. |

Abbreviations

| Abbreviation | Clarification |
| --- | --- |
| SCADA | Supervisory Control and Data Acquisition |
| HMI | Human Machine Interface |
| IED | Intelligent Electronic Device |
| RTU | Remote Terminal Unit |
| PLC | Programmable Logic Controller |
| RPO | Recovery Point Objective |
| RTO | Recovery Time Objective |
| ILRA | Initial Level Risk Assessment |
| HLRA | High Level Risk Assessment |
| SuC | System under Consideration |
| SNMP | Simple Network Management Protocol |
| UDP | User Datagram Protocol |
| TCP | Transmission Control Protocol |
| Syslog | System Logging Protocol |
| RADIUS | Remote Authentication Dial-In User Service |
| DNP3 | Distributed Network Protocol version 3 |
| LDAP | Lightweight Directory Access Protocol |
| MMS | Manufacturing Message Specification |
| PTPv2 | Precision Time Protocol Version 2 |
| GOOSE | Generic Object Oriented Substation Event |
| MFA | Multi-Factor Authentication |

Applicable Documents

Related Documents

| No | Doc Code | Employer Doc Code | Doc Title | Ver |
| --- | --- | --- | --- | --- |
| 1 |  |  | Simple Network Diagram | 1 |
| 2 |  |  | Dataflow Diagram | 1 |

Project Asset and SuC Description

System Under Consideration

A substation is a complex system consisting of various components such as transformers, capacitors, voltage regulators, and circuit breakers. In smart grid systems, automated substation control will be widely implemented to enable real-time monitoring and control via local area networks. Figure 1 illustrates the system architecture of a substation.

Figure 1	The system architecture diagram of the substation

Substations are crucial for ensuring the stability of electrical supply and load management across low, medium, and high voltage distribution networks. To maintain the efficient operation of substations and associated equipment, such as line-mounted switches and capacitors, utilities typically rely on SCADA (Supervisory Control and Data Acquisition) systems for automated monitoring and control.

New installations generally incorporate SCADA systems to oversee and manage substations and their components. However, older facilities can also benefit from adopting or upgrading SCADA systems to leverage the latest technologies. A new or upgraded SCADA system not only enhances monitoring and control capabilities but also extends the lifespan of substations and related equipment by providing real-time data for identifying and addressing minor issues before they escalate. Additionally, the wealth of historical data generated by SCADA systems aids in optimizing preventive maintenance schedules, reducing related costs.

Electrical distribution systems often consist of numerous remote locations, and managing these sites has traditionally been challenging. To address this, utilities began deploying remote terminal units (RTUs) at substations. Initially custom-built, RTUs evolved to incorporate standard hardware such as programmable logic controllers (PLCs) or industrial PCs. More recently, intelligent electronic devices (IEDs) have become prevalent in substations, typically communicating with the RTU to enhance data collection and control functions.

Switchgear feeders control power distribution to various electrical loads at substations, and sensors on the switchgear capture critical data such as current, voltage, power, and operational status. This data is transmitted to the RTU and subsequently polled by the SCADA system.

A SCADA system typically consists of a master control station with one or more PC-based human-machine interfaces (HMIs). In larger substations, additional secondary control stations with HMIs may be present, along with local HMIs for on-site operators. These operators use the HMIs to monitor and manage substation operations and related equipment. Modern SCADA systems are highly efficient at processing vast amounts of data necessary for tracking the operational status of power lines, cables, and equipment, ensuring optimal performance and reliability.

The Assets of SuC

The initial assets of the system under consideration (SuC) for this project include the following:

SCADA System

- SCADA Server

- Gateway

- HMI

- IED (Bay Control Unit)

- Ethernet Switch

Safety Control System

- IED (Protection Relay)

- Ethernet Switch

Configuration & Auxiliary Management System

Wireless Access Point (capable of connecting to a laptop)

HLRA updated Network Diagram

Figure 2, titled "Simple Network Diagram of the SuC," presents the revised network architecture following the HLRA (High Level Risk Assessment). This diagram incorporates the segmentation of zones and conduits as identified through the analysis. Additionally, it outlines the preliminary set of required security countermeasure equipment. For comprehensive details, please refer to the document "ICP 2L Lab – Simple Network Diagram.pdf".

Figure 2	The system architecture diagram of the substation

SuC dataflow diagram

The data flow diagram of the SuC is illustrated in Figure 3 – Data Flow Diagram of the SuC. Following the ILRA analysis and the segmentation of zones and conduits, the diagram also preliminarily indicates the required security countermeasure equipment.

For further details, please refer to ICP 2L Lab Dataflow Diagram.pdf.

Figure 3	The Dataflow diagram of the substation

| No | Description | From | To | Protocol | Type | Port |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | Receive monitoring status from network devices. | HW-01-001 HW-01-002 HW-01-003 HW-02-007 HW-02-008 HW-02-009 HW-02-010 | HW-02-001 HW-02-002 | SNMP | UDP | 162 |
| 2 | Receive logs from network devices. | HW-01-001 HW-01-002 HW-01-003 HW-02-007 HW-02-008 HW-02-009 HW-02-010 | HW-02-001 HW-02-002 | Syslog | UDP | 514 |
| 3 | Used for authentication and authorization logging. | HW-01-001 HW-01-002 HW-01-003 HW-02-007 HW-02-008 HW-02-009 HW-02-010 | HW-02-001 HW-02-002 | RADIUS | UDP | 1812, 1813 |
| 4 | Provide monitoring for the Taipower Dispatch Center. | HW-02-003 HW-02-004 | TPC ADCC | DNP3 | TCP | 20000 |
| 5 | Provide display and data to the HMI. | HW-02-001 HW-02-002 | HW-04-002 | WebSocket | TCP | 33333 |
| 6 | SCADA performs operations on the database. | HW-02-001 HW-02-002 | HW-02-006 | MySQL | TCP | 3306` |
| 7 | Provide UPS transmission status and alarms. | HW-02-011 | HW-02-001 HW-02-002 | SNMP | UDP | 162 |
| 8 | Provide authentication and authorization for IED devices. | HW-02-015 HW-02-016 HW-02-017 HW-02-018 HW-02-019 HW-02-020 HW-03-003 HW-03-004 HW-03-005 | HW-02-001 HW-02-002 | LDAP | TCP | 389 |
| 9 | IEDs send signals back to the system via IEC 61850 Protocol. | HW-02-015 HW-02-016 HW-02-017 HW-02-018 HW-02-019 HW-02-020 HW-03-003 HW-03-004 HW-03-005 | HW-02-001 HW-02-002 HW-02-003 HW-02-004 | MMS | TCP | 102 |
| 10 | Provide time synchronization for IED devices. | HW-02-010 | HW-02-015 HW-02-016 HW-02-017 HW-02-018 HW-02-019 HW-02-020 HW-03-003 HW-03-004 HW-03-005 | PTPv2 | Broadcast | N/A |
| 11 | Implement protection coordination between IED devices. | HW-02-015 HW-02-016 HW-02-017 HW-02-018 HW-02-019 HW-02-020 HW-03-003 HW-03-004 HW-03-005 | HW-02-015 HW-02-016 HW-02-017 HW-02-018 HW-02-019 HW-02-020 HW-03-003 HW-03-004 HW-03-005 | GOOSE | Multicast | N/A |

Defense-in-Depth Architecture of the SuC

The defense-in-depth architecture of the SuC is designed based on layered security principles and follows the Purdue Enterprise Reference Architecture. The implementation includes the following key security controls:

From Outside Zone to Purdue Level 3

- Deploy a firewall to restrict permitted asset and service connections from the Substation Zone to the Supervisory and Service Zones.

- Enforce multi-factor authentication (MFA) for any connection initiated from the Substation Zone.

- Ensure encryption is applied to all connections originating from the Substation Zone.

- Deploy a firewall to restrict permitted asset and service connections from the Working Zone to the Supervisory Zone.

- Apply secure access controls for web-based services accessed from the Working Zone to the Supervisory Zone.

- Encrypt all connections originating from the Working Zone.

From Purdue Level 3 to Purdue Level 2

Deploy a managed switch with an enforced asset whitelist to restrict asset and service connections from the Service Zone to the Supervisory, Safety, and Control Zones.

From Purdue Level 2 to Purdue Level 1

- Deploy a router with firewall functionality and asset whitelisting to restrict connections from the Service Zone and Supervisory Zone to the Safety and Control Zones.

- Configure firewall rules on the router to strictly limit permitted asset and service connections from the Supervisory Zone to the Safety Zone.